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NFPA 80 Fire Door and Hardware Inspection Checklist
1.0 Form Objective & Regulatory Context
This Fire Door and Hardware Inspection Checklist is designed to verify compliance with NFPA 80: Standard for Fire Doors and Other Opening Protectives. It ensures that fire doors, frames, and hardware are properly installed, maintained, and operational to contain fire and smoke in industrial and manufacturing environments. This form satisfies WorkSafeBC requirements for fire protection systems and annual inspection mandates.
2.0 Administrative Details
Date of Inspection: ____________________
Time of Inspection: ____________________
Inspector Name: ____________________
Facility Name: ____________________
Building/Location: ____________________
Fire Door ID Number: ____________________
3.0 Audit / Inspection Items
☐ Pass  ☐ Fail - Verify fire door label is present and legible.
☐ Pass  ☐ Fail - Inspect door frame for damage, warping, or corrosion.
☐ Pass  ☐ Fail - Check door clearance at bottom (max 3/4 inch) and sides (max 1/8 inch).
☐ Pass  ☐ Fail - Confirm self-closing device operates fully and closes door completely.
☐ Pass  ☐ Fail - Test latching hardware: door latches securely without binding.
☐ Pass  ☐ Fail - Inspect hinges for tightness, damage, and proper alignment.
☐ Pass  ☐ Fail - Verify door is free of obstructions (e.g., wedges, stops) that prevent closure.
☐ Pass  ☐ Fail - Check for gaps or holes in door or frame that could compromise fire rating.
☐ Pass  ☐ Fail - Inspect gasketing and seals for wear or damage.
☐ Pass  ☐ Fail - Confirm door swings in correct direction per fire plan.
☐ Pass  ☐ Fail - Test panic hardware (if applicable) for proper operation.
☐ Pass  ☐ Fail - Verify door is not painted or coated in a way that obscures label or affects operation.
4.0 Corrective Actions & Deficiencies
Issue Description: ________________________________________
Location of Deficiency: ________________________________________
Immediate Action Taken: ________________________________________
Corrective Action Required: ________________________________________
Assigned To: ________________________________________
Due Date: ________________________________________
5.0 Sign-off & Authorization
Inspector Signature: __________________________ Date: ____________
Facility Manager Signature: __________________________ Date: ____________
Safety Officer Signature (if applicable): __________________________ Date: ____________

Regulatory Disclaimer: This audit log is a generic safety template. The end-user assumes all liability for validating all inspection parameters against WorkSafeBC, OH&S, and specific equipment manuals before active shop floor deployment.
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