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Elevator Machine Room Visual Inspection Code Compliance Log
1.0 Form Objective & Asset Scope
This Elevator Machine Room Visual Inspection Code Compliance Log is designed to document the condition and compliance of elevator machine rooms in accordance with ASME A17.1/CSA B44 safety codes. It tracks critical parameters such as lighting, ventilation, clearances, fire protection, and equipment condition to ensure safe operation and regulatory adherence. This log is essential for facility reliability engineers and maintenance technicians to identify deficiencies before they lead to equipment failure or safety violations.
2.0 Administrative & Asset Details
Date of Inspection: ____________________
Inspector Name: ____________________
Building Name / Address: ____________________
Elevator Machine Room ID / Location: ____________________
Elevator Unit Number(s) Served: ____________________
Inspection Type (Routine / Annual / Post-Repair): ____________________
3.0 Inspection / Parameter Checklist
☐ Pass  ☐ Fail - Verify machine room door is self-closing, self-locking, and labeled 'Elevator Machine Room – No Storage'.
☐ Pass  ☐ Fail - Check that room lighting provides minimum 50 lux at floor level and emergency lighting is functional.
☐ Pass  ☐ Fail - Confirm ventilation or air conditioning maintains ambient temperature between 10°C and 40°C.
☐ Pass  ☐ Fail - Inspect for adequate clearances around equipment per code (minimum 600 mm working space).
☐ Pass  ☐ Fail - Verify fire extinguisher is present, accessible, and within current inspection date.
☐ Pass  ☐ Fail - Check that no combustible materials or unauthorized storage are present in the room.
☐ Pass  ☐ Fail - Inspect machine room floor for oil leaks, debris, or tripping hazards.
☐ Pass  ☐ Fail - Verify that all electrical panels are closed, labeled, and free of corrosion or damage.
☐ Pass  ☐ Fail - Check that governor and machine sheaves are free of excessive wear or unusual noise.
☐ Pass  ☐ Fail - Confirm that all safety switches (e.g., stop switch, inspection switch) are accessible and labeled.
☐ Pass  ☐ Fail - Inspect that machine room is free of water leaks, condensation, or signs of pest infestation.
☐ Pass  ☐ Fail - Verify that all required code signage (e.g., 'No Smoking', 'High Voltage') is posted and legible.
4.0 Deficiencies & Work Order Generation
Deficiency Description (include code reference if applicable): ________________________________________
Corrective Action Required: ________________________________________
Parts or Materials Needed: ________________________________________
Priority Level (Critical / High / Medium / Low): ________________________________________
Assigned To: ________________________________________
Target Completion Date: ________________________________________
5.0 Sign-off & Return to Operations
Inspector Signature: __________________________ Date: ____________
Facility Reliability Engineer Review: __________________________ Date: ____________
Elevator Contractor (if applicable): __________________________ Date: ____________

Regulatory Disclaimer: This maintenance log is a generic template. The end-user assumes all liability for validating all inspection parameters, PM frequencies, and tolerances against specific OEM machinery manuals before active shop floor deployment.
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