| [ INSERT YOUR COMPANY NAME HERE ] Maintenance Standard Operating Procedure | Created By: ____________________ Verified By: ____________________ Version: 1.0 · Est. Time: 45 min |
| --- | --- |

Forklift Battery Charging and Watering Station Safety Inspection and Maintenance

1.0 Maintenance Objective & Frequency

The objective of this procedure is to perform a weekly safety inspection and preventive maintenance on the forklift battery charging and watering station. This includes verifying the integrity of charging cables and connectors, checking electrolyte levels in lead-acid batteries, ensuring proper ventilation and spill containment, and confirming that emergency eyewash/shower equipment is functional. Proper execution prevents electrical arcing, acid burns, hydrogen gas accumulation, and premature battery failure.

Frequency: Weekly (every 40 operating hours or as scheduled by the facility CMMS). Additional checks are required after any battery change-out or if a charging fault is reported.

2.0 Lockout/Tagout (LOTO) & Safety

• Electrical Isolation: Turn off the main disconnect switch for the charging station. Lock and tag the disconnect in the OFF position. Verify zero voltage at the charger output terminals using a calibrated multimeter. • Battery Isolation: Ensure all battery connectors are disconnected from the charger and from each other. Do not work on a battery that is actively charging. • Hydrogen Gas Hazard: Verify that the ventilation system (exhaust fan or passive vents) is operational and unobstructed. No smoking, open flames, or sparks are permitted within 3 metres of the charging area. • PPE Requirements: Wear acid-resistant gloves, safety goggles with side shields, a rubber apron, and steel-toed rubber boots. Keep a face shield nearby for electrolyte handling. • Spill Response: Confirm that a neutralizing agent (e.g., baking soda or commercial acid spill kit) is present and within reach. The eyewash station must be flushed and verified to provide 15 minutes of continuous flow.

3.0 Required Tools, Parts & Lubricants

▪  Calibrated digital multimeter (CAT III / 600V minimum)

▪  Distilled water (battery grade, sealed container)

▪  Battery hydrometer or refractometer (for specific gravity check)

▪  Non-metallic funnel or automatic watering gun

▪  Clean lint-free rags and acid-resistant brush

▪  Baking soda (sodium bicarbonate) for neutralization

▪  Torque wrench (0-30 Nm range) with insulated socket

▪  Replacement charging connector (if damaged)

▪  Personal protective equipment (acid gloves, goggles, apron, face shield)

▪  Lockout/tagout kit and padlock

4.0 Step-by-Step Maintenance Procedure

1.  Perform LOTO: Isolate the charging station at the main disconnect. Lock and tag. Verify zero voltage at the charger output terminals with a multimeter.

2.  Inspect the charging cables and connectors for cuts, abrasions, corrosion, or loose pins. Replace any damaged connectors. Tighten terminal bolts to 12 Nm using an insulated torque wrench.

3.  Check the charger housing and cooling vents for dust or debris buildup. Clean with a dry brush or compressed air (max 30 psi) if necessary. Ensure the cooling fan spins freely.

4.  Remove the battery vent caps (if applicable) and inspect electrolyte levels in each cell. The electrolyte must cover the plates by 10-15 mm. Do not overfill.

5.  Top off low cells with distilled water only. Use a non-metallic funnel or automatic watering gun. Never add acid unless the battery has been spilled and neutralized.

6.  Measure the specific gravity of each cell using a hydrometer or refractometer. Record the readings. A variation greater than 0.030 between cells indicates a failing battery.

7.  Inspect the battery case for cracks, bulges, or signs of acid leakage. Neutralize any acid residue with a baking soda solution (1 kg baking soda per 10 L water) and rinse with clean water.

8.  Check the ventilation system: verify that the exhaust fan operates when the charger is on and that intake vents are clear. Measure airflow at the fan outlet (minimum 0.5 m/s face velocity).

9.  Test the emergency eyewash station by activating the flush for 15 seconds. Confirm that the water stream is clear and that the unit delivers tepid water (16-38°C). Record the date on the inspection tag.

10.  Inspect the spill containment berm or floor coating for cracks or saturation. Replace absorbent pads if present and saturated. Ensure the spill kit is fully stocked.

11.  Reinstall all battery vent caps securely. Wipe down the battery top and charger exterior with a clean rag. Remove all tools and debris from the work area.

12.  Remove LOTO tags and locks. Restore power to the charging station. Perform a functional test by connecting a known-good battery and initiating a charge cycle. Verify that the charger displays normal voltage and current readings.

5.0 Verification & Return to Service

1.  Confirm that the charger completes a full charge cycle without fault codes or overheating. Monitor the battery temperature during charging (max 55°C).

2.  Verify that the ventilation system remains operational throughout the charge cycle. Listen for abnormal fan noise.

3.  Document all readings (specific gravity, voltage, electrolyte levels, ventilation airflow) in the CMMS work order. Note any corrective actions taken.

4.  Sign off on the PM work order in ServiceGrid. Attach photos of the completed inspection if required by facility policy.

5.  Return the charging station to service. Notify the shift supervisor that the station is safe for use.

Regulatory Disclaimer: This document is a generic maintenance template provided for educational and informational purposes only. It does not constitute professional engineering or reliability advice. The end-user assumes all liability for validating all step sequences, torque specs, and LOTO protocols against specific machinery OEM manuals before deployment to a live production floor.