| [ INSERT YOUR COMPANY NAME HERE ] Technical Material Specification | Created By: ____________________ Verified By: ____________________ Version: 1.0 |
| --- | --- |

100% Silicone Sealant – Technical Material Specification

1.0 Material Overview & Common Uses

100% silicone sealant is a one-component, moisture-curing, elastomeric sealant composed primarily of polydimethylsiloxane (PDMS) polymers, crosslinkers, and reinforcing fillers. It contains no solvents, urethanes, or acrylics, and cures by reacting with atmospheric humidity to form a flexible, durable rubber seal.

▪  Primary applications include sealing joints in building envelopes (windows, doors, curtain walls), sanitary sealing in kitchens and bathrooms, bonding and sealing in HVAC ductwork, and gasketing in electrical enclosures.

▪  Commonly used in automotive assembly for weatherstripping and windshield bonding, and in marine applications for above-waterline sealing.

▪  Available in neutral cure (non-corrosive to metals) and acetoxy cure (releases acetic acid, not for use on copper, brass, or natural stone).

2.0 Core Technical Properties & Sizing

▪  Density (uncured): 1.02 – 1.05 g/cm³ at 25°C.

▪  Tensile strength (cured): 1.5 – 2.5 MPa (ASTM D412).

▪  Elongation at break: 300 – 600% (ASTM D412).

▪  Hardness (Shore A): 20 – 30 (ASTM D2240).

▪  Service temperature range: -50°C to +200°C continuous, intermittent up to 250°C.

▪  Tack-free time: 10 – 30 minutes at 23°C / 50% RH (varies by formulation).

▪  Full cure time: 24 hours per 3 mm depth at 23°C / 50% RH.

▪  Standard packaging: 300 ml cartridges (plastic or aluminum), 600 ml sausage packs, 20 L pails, and 200 L drums.

▪  Shelf life: 12 months from date of manufacture when stored below 30°C.

3.0 Processing, Machinability & Application

100% silicone sealant is applied using manual or pneumatic caulking guns, bulk dispensing equipment, or robotic applicators. Surface preparation is critical for adhesion: substrates must be clean, dry, and free of oil, grease, dust, and loose particles. Priming is required on porous substrates (concrete, masonry, wood) and some plastics.

▪  Application temperature range: +5°C to +40°C (substrate and ambient). Do not apply below dew point.

▪  Tooling must be completed within 5 minutes of application using a spatula or tooling agent (soapy water or isopropyl alcohol).

▪  For structural glazing applications, use only neutral-cure silicone with documented adhesion testing per ASTM C1135.

▪  Do not thin or dilute with solvents; this will compromise cure and mechanical properties.

▪  For thick-section applications (> 10 mm depth), use a two-part silicone system to ensure complete cure.

▪  Cured silicone can be cut with a sharp knife or razor blade; it cannot be sanded or machined effectively.

4.0 Common Defects & Quality Control

▪  Reject if sealant has visible skinning or partial cure inside the cartridge (indicates cap failure or age degradation).

▪  Reject if sealant exhibits phase separation (liquid exudate on surface) or excessive oil bleed-out.

▪  Reject if cured sealant shows cracking, cohesive failure, or adhesion loss within 7 days of application under standard conditions.

▪  Reject if uncured sealant has lumps, grittiness, or foreign particles visible to the naked eye.

▪  Acceptable joint dimensions: width-to-depth ratio between 2:1 and 3:1 for dynamic joints; maximum depth 12 mm for single-stage application.

▪  Perform adhesion pull-off test per ASTM C794 on representative substrate samples before production runs.

5.0 Storage, Handling & WHMIS Guidelines

• Store in a cool, dry area below 30°C and out of direct sunlight. Do not freeze (some formulations may be damaged below 5°C). • Maintain relative humidity below 70% in storage area to prevent premature curing of opened containers. • Follow FIFO (First-In, First-Out) inventory rotation; shelf life is 12 months from date of manufacture. • WHMIS 2015 Classification: Not classified as hazardous under normal use. However, acetoxy-cure formulations release acetic acid vapour during cure – use in well-ventilated areas. • Mandatory PPE: Wear nitrile gloves to prevent skin contact; safety glasses recommended during application. If skin contact occurs, wash with soap and water. • In case of eye contact, flush with water for 15 minutes and seek medical attention. • Dispose of cured silicone as non-hazardous industrial waste per local regulations. Uncured material should be cured before disposal.

Regulatory Disclaimer: This document is a generic technical material specification provided for educational purposes. The end-user assumes all liability for reviewing, adapting, and validating all tolerances, properties, and safety protocols against specific OEM data sheets and local regulations before deployment.